## Cover
UPS2000-G-(6K-20K) V100R001 Installation Standard Operating Procedure (SOP) V2.0
Revision Declaration
Prepared and interpreted by:
Specifications or documents related to this specification:
Conformance with related international specifications or documents:
This document replaces:
Relations with other specifications or documents:
Version | Prepared by | Reviewed by | Approved by | Description | Date
V1.0 | songjiao | niujianxun | wangwenhua
V2.0 | qinzhifang | niujianxun
Huawei Technologies Co., Ltd.
All rights reserved

## Installation Scenarios
Installation Scenarios:
Rack-mounting a single UPS2000-G-6 kVA or UPS2000-G-10 kVA
Tower-mounting a single UPS2000-G-6K or UPS2000-G-10K
Rack-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel
Tower-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA
Tower-mounting a single UPS2000-G-15K or UPS2000-G-20K
Rack-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel
Tower-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel

## Standard Operating Procedure
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | [6 empty] | 1.3.1 |  | 1.4.1 |  | 1.5.1 |  | 1.6.1 |  |  |  |  | 1.8.1
[7 empty] | Rack-mounting a single UPS2000-G-6 kVA or UPS2000-G-10 kVA |  | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  |  |  |  | Starting the UPS in Normal Mode
[7 empty] | 0:20 | 0:35 | 0:35:0000 | 1:00 | 1:00 | 1:10 | 1:10 | 1:20 |  |  |  | 1:40 | 2:00
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB |  |  |  | Installation personnel | AB
| 1.1 |  | 1.2 | [11 empty] | 1.7
| Installation preparations and environment acceptance |  | Unpacking and checking | [11 empty] | Checking Before Powering On the UPS
| 0:00 | 0:10 | 0:10 | 0:20 | [10 empty] | 1:20 | 1:40
| Installation personnel | AB | Installation personnel | AB | [10 empty] | Installation personnel | AB
[7 empty] | 1.3.2 |  | 1.4.2 |  | 1.5.2 |  | 1.6.2 |  |  |  |  | 1.8.2
[7 empty] | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  | Tower-mounting a single UPS2000-G-6K or UPS2000-G-10K |  |  |  |  | Starting the UPS in Battery Mode
[7 empty] | 0:20 | 0:45 | 0:45 | 0:55 | 0:55 | 1:05 | 1:05 | 1:20 |  |  |  | 1:40 | 2:00
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB |  |  |  | Installation personnel | AB
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | [6 empty] | 1.3.1 |  | 1.4.1 |  | 1.5.1 |  | 1.6.1 |  |  |  |  | 1.8.1
[7 empty] | Rack-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel |  | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  |  |  |  | Starting the UPS in Normal Mode
[7 empty] | 0:20 | 0:50 | 0:50 | 1:30 | 1:30 | 1:50 | 1:50 | 2:00
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB |  |  |  | 2:20 | 4:00
| 1.1 |  | 1.2 | [11 empty] | 1.7 |  |  | Installation personnel | AB
| Installation preparations and environment acceptance |  | Unpacking and checking | [11 empty] | Checking Before Powering On the UPS
| 0:00 | 0:10 | 0:10 | 0:20 | [10 empty] | 2:00 | 2:20
| Installation personnel | AB | Installation personnel | AB | [10 empty] | Installation personnel | AB
[7 empty] | 1.3.2 |  | 1.4.2 |  | 1.5.2 |  | 1.6.2
[7 empty] | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  | Tower-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel |  |  |  |  | 1.8.2
[7 empty] | 0:20 | 1:00 | 1:00 | 1:20 | 1:20 | 1:30 | 1:30 | 2:00 |  |  |  | Starting the UPS in Battery Mode
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB
[18 empty] | 2:20 | 4:00
Installing a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | [6 empty] | 1.3.1 |  | 1.4.1 |  | 1.5.1 |  | 1.6.1 |  |  |  |  | Installation personnel | AB
[7 empty] | Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA |  | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch
[7 empty] | 0:20 | 0:35 | 0:35:0000 | 1:00 | 1:00 | 1:10 | 1:10 | 1:20
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB
| 1.1 |  | 1.2 | [11 empty] | 1.7 |  | 1.7
| Installation preparations and environment acceptance |  | Unpacking and checking | [11 empty] | Checking Before Powering On the UPS |  | Starting the UPS in Normal Mode
| 0:00 | 0:10 | 0:10 | 0:20 | [10 empty] | 1:20 | 1:40 | 1:40 | 2:00
| Installation personnel | AB | Installation personnel | AB | [10 empty] | Installation personnel | AB | Installation personnel | AB
[7 empty] | 1.3.2 |  | 1.4.2 |  | 1.5.2 |  | 1.6.2
[7 empty] | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  | Tower-mounting a single UPS2000-G-15K or UPS2000-G-20K
[7 empty] | 0:20 | 0:45 | 0:45 | 0:55 | 0:55 | 1:05 | 1:05 | 1:20
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | [6 empty] | 1.3.1 |  | 1.4.1 |  | 1.5.1 |  | 1.6.1
[7 empty] | Rack-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel |  | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch
[7 empty] | 0:20 | 0:50 | 0:50 | 1:30 | 1:30 | 1:50 | 1:50 | 2:00
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB
| 1.1 |  | 1.2 | [11 empty] | 1.7 |  | 1.7
| Installation preparations and environment acceptance |  | Unpacking and checking | [11 empty] | Checking Before Powering On the UPS |  | Starting the UPS in Normal Mode
| 0:00 | 0:10 | 0:10 | 0:20 | [10 empty] | 2:00 | 2:20 | 2:20 | 4:00
| Installation personnel | AB | Installation personnel | AB | [10 empty] | Installation personnel | AB | Installation personnel | AB
[7 empty] | 1.3.2 |  | 1.4.2 |  | 1.5.2 |  | 1.6.2
[7 empty] | Connecting power cables |  | Connecting communications cables |  | Connecting the emergency power-off (EPO) switch |  | Tower-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel
[7 empty] | 0:20 | 1:00 | 1:00 | 1:20 | 1:20 | 1:30 | 1:30 | 2:00
[7 empty] | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB | Installation personnel | AB
Installing battery pack (ESS-240V12-(9AhBPVBA and 7AhBPVBA)) |  |  |  | 1.2.1 |  |  | 1.3.1
|  |  |  | Rack-mounting |  |  | Connecting power cables
|  |  |  | 0:10 | 0:25 |  | 0:25 | 0:50
|  |  |  | Installation personnel | AB |  | Installation personnel | AB
1.1
Unpacking and checking
| 0:00 | 0:10
| Installation personnel | AB
|  |  |  | 1.2.2 |  |  | 1.3.2
|  |  |  | Connecting power cables |  |  | Tower-mounting
|  |  |  | 0:10 | 0:35 |  | 0:35 | 0:50
|  |  |  | Installation personnel | AB |  | Installation personnel | AB
Installing PDU (PDC-0091V2ACIOA) | 1.1 |  | 1.2 |  |  | 1.3
| Unpacking and checking |  | Rack-mounting |  |  | Connecting power cables
| 0:00 | 0:10 | 0:10 | 0:25 |  | 0:25 | 0:50
| Installation personnel | AB | Installation personnel | AB |  | Installation personnel | AB
Installing PDU (PDC-0038V4ACIOA) | 1.1 |  | 1.2 |  |  | 1.3
| Unpacking and checking |  | Rack-mounting |  |  | Connecting power cables
| 0:10 | 0:20 | 0:10 | 0:25 |  | 0:25 | 0:50
| Installation personnel | AB | Installation personnel | AB |  | Installation personnel | AB
Installing Industrial-Frequency Transformer(DGL-6 & DGL-10) | 1.1 |  | 1.2 |  |  | 1.3
| Unpacking and checking |  | Rack-mounting |  |  | Connecting power cables
| 0:10 | 0:20 | 0:20 | 0:35 |  | 0:35 | 1:00
| Installation personnel | AB | Installation personnel | AB |  | Installation personnel | AB
NOTE：UPS support Rack-mounting or Tower-mounting.
Method 1: Rack-mounting
Start
Start
Start
Start
Start
Start
Start
Method 2: Tower-mounting
Method 1: Rack-mounting
Method 2: Tower-mounting
Method 1: Rack-mounting
Method 2: Tower-mounting
Method 1: Rack-mounting
Method 2: Tower-mounting
Method 1: Rack-mounting
Method 2: Tower-mounting
Start

## Installation Tools
UPS2000-G标准安装工具
Clamp meter
COAX crimping tool
Multimeter
Label
Flat-head screwdriver (2 mm x 80 mm)
Diagonal pliers
Wire stripper
ESD gloves
Polyvinyl chloride (PVC) insulation tape
Hydraulic pliers
Insulated gloves
Cotton cloth
Heat shrink tubing (Ф14, Ф18, Ф20, or Ф25)
Protective gloves
Cable tie
Electrician's knife
Brush
Heat gun
Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm)
Claw hammer

## Single UPS 6kVA or 10kVA
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Installation preparations and environment acceptance |  |  | AB |  | 10min
Preparations
| 1 | Install cable trays properly in the equipment room.
| 2 | Check the installation position and direction of the cabinet, make sure it does not interfere with maintenance space of surrounding equipment, and place equipment along the same line to facilitate cabling and maintenance.
| 3 | Install the UPS2000-G-6 kVA or UPS2000-G-10 kVA in environments with proper ventilation and far away from water, heat sources, and flammable or explosive materials. Check that the UPS2000-G-6 kVA or UPS2000-G-10 kVA is free from direct sunlight, dust, volatile gases, corrosive materials, and salty air.
| 4 | Check that the front and rear panels are at least 60 cm away from walls and adjacent equipment. Check that the ventilation holes in the front and rear panels are not blocked. Temperature rise caused by poor ventilation inside the UPS2000-G-6 kVA or UPS2000-G-10 kVA will shorten the service life.
| 5 | Check that the neutral-ground voltage is less than or equal to 5 V AC.
6
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.1 |  | Rack-mounting a single UPS2000-G-6 kVA or UPS2000-G-10 kVA |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting ears on both sides of the UPS2000-G-6 kVA or UPS2000-G-10 kVA according to instructions. Determine the position for installing the UPS2000-G-6 kVA or UPS2000-G-10 kVA based on its dimensions for rack-mounting.
| 2 | Install adjustable guide rails or floating nuts.
| 3 | Place the UPS on the guide rails. Secure the UPS to the rack using M6x16TM screws through the holes in the mounting brackets.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
2
3
4
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 | Flat-head screwdriver (2 mm x 80 mm) |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-6 kVA or UPS2000-G-10 kVA
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.2/1.4.1 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Open UPS AC input circuit breaker,loosen screws to remove the terminal cover and battery port cover.
| 2 | Connect cables in this sequence: AC output power cables, AC input power cables, and battery cables.
3
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | . For single-phase AC inputs of UPS2000-G-10 kVA, use short-circuit busbars to connect L1, L2, and L3 of AC input power cables.
| 3 | In single UPS mode, AC OUTPUT sL connects to primary loads, which require uninterruptible power supply, and pL connects to secondary loads, which require high quality power supply.
| 4 | Install a DC circuit breaker between the battery string and the UPS battery port.
| 5 | In single UPS mode, if power segment is enabled, pL is disconnected and sL continues with power output when an overload occurs
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Battery cables |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.4.2/1.5.1 |  | Connecting communications cables |  |  | AB |  | 10min
Installation Procedure
| 1 | (Optional) Connect cables to SNMP card: a. Temperature and humidity monitoring port (TEM_HUM): Connect one end of the cable to the temperature and humidity monitoring port on the Simple Network Management Protocol (SNMP) card and the other end to the ambient temperature and humidity sensor. b. Fast Ethernet (FE) port: Connect one end of the cable to the FE port on the SNMP card and the other end to the Ethernet.
| 2 | (Optional) Connect cables to modbus card: a. Connect the COM_1 port (the COM_2 port is used for cascading) on the Modbus card to the RS485 port on the RS232-RS485 adapter over an RS485 cable. b. Connect the RS232 port on the RS232-RS485 adapter to the RS232 port on the PC over an RS232 cable.
| 3 | (Optional) Connect cables to dry contact card card: Connect one end of the cable to the dry contact card and the other end to the customer equipment.
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
| 2 | In the figure of modbus car, the two UPSs represent two separate single UPS systems.
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.5.2/1.6.1 |  | Connecting the emergency power-off (EPO) switch |  |  | AB |  | 10min
Installation Procedure
| 1 | Connect cables to EPO ports. This procedure is required if the UPS2000-G-6 kVA or UPS2000-G-10 kVA is configured with components that enable the EPO function.
2
3
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.6.2 |  | Tower-mounting a single UPS2000-G-6K or UPS2000-G-10K |  |  | AB |  | 15min
Installation Procedure
| 1 | Adjust the control panel and logo directions. Press the grooves on both sides of the front panel, and remove the front panel horizontally with even force. Rotate the control panel 90 degrees anticlockwise. Reinstall the front panel. Rotate the logo on the front panel 90 degrees anticlockwise.
| 2 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically, as shown in the following figure.
| 3 | Install two groups of support bases for each group of devices as follows: Place support bases on the floor, determine the distance (greater than or equal to 280 mm) between the two groups of support bases, place devices on the support bases in sequence, and secure them.
| 4 | After the UPS is tower-mounted, seal the four screw holes on the top with rubber plugs that are delivered with the UPS.
5
6
Key Techniques
| 1 | To ensure that the UPS2000-G-6 kVA or UPS2000-G-10 kVA attaches firmly to the bases, a distance of at least 280 mm is recommended for two neighboring bases. The distance should not exceed the UPS2000-G1-6K or UPS2000-G1-10K depth.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | UPS2000-G-6 kVA or UPS2000-G-10 kVA |  |  | 2 | UPS2000-G-6 kVA or UPS2000-G-10 kVA support bases
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.7 |  | Checking Before Powering On the UPS |  |  | AB |  | 20min
Installation Procedure
| 1 | AC power cable colors comply with local electrical regulations.
| 2 | Cables are securely connected.
| 3 | The battery terminals are connected correctly, and the voltages comply with industry standards.
| 4 | Power cables and signal cables are correctly identified.
| 5 | Cables are neatly routed and securely bound.
| 6 | Devices are installed and cables are routed in ways that facilitate modification, capacity expansion, and maintenance.
| 7 | The UPS is properly grounded.
| 8 | The voltage between the neutral wire and the ground cable is less than 5 V AC.
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.1 |  | Starting the UPS in Normal Mode |  |  | AB |  | 20min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Close the AC input circuit breaker K1.The initialization screen is displayed.Set the language (the preset language is English), system parameters, and battery parameters.
| 3 | Start the UPS in normal mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | To prevent triggering overload protection, start the loads with higher power and then loads with lower power.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing a single UPS2000-G-6 kVA or UPS2000-G-10 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.2 |  | Starting the UPS in Battery Mode |  |  | AB |  | 20min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Press . The initialization screen is displayed. Set the language (the preset language is English), system parameters, and battery parameters.
| 3 | Perform "startup operations" on the UPS.The UPS enters battery mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | To prevent triggering overload protection, start the loads with higher power and then loads with lower power.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
划线辅助板板
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装螺栓、弹垫、平垫在绝缘垫片上.
安装螺栓、弹垫、平垫在绝缘垫片上.
Connecting Power Cables to the UPS2000-G-10 kVA (Single-Phase Input Single-Phase Output)
Connecting Power Cables to the UPS2000-G-10 kVA (Three-Phase Input Single-Phase Output)
Connect cables to SNMP card
Connect cables to modbus card
Connect cables to dry contact card card
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
Connecting Power Cables to the UPS2000-G-6 kVA (Single-Phase Input Single-Phase Output)
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步

## 6kVA or 10kVA in parallel
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Installation preparations and environment acceptance |  |  | AB |  | 10min
Preparations
| 1 | Install cable trays properly in the equipment room.
| 2 | Check the installation position and direction of the cabinet, make sure it does not interfere with maintenance space of surrounding equipment, and place equipment along the same line to facilitate cabling and maintenance.
| 3 | Install the UPS2000-G-6 kVA or UPS2000-G-10 kVA in environments with proper ventilation and far away from water, heat sources, and flammable or explosive materials. Check that the UPS2000-G-6 kVA or UPS2000-G-10 kVA is free from direct sunlight, dust, volatile gases, corrosive materials, and salty air.
| 4 | Check that the front and rear panels are at least 60 cm away from walls and adjacent equipment. Check that the ventilation holes in the front and rear panels are not blocked. Temperature rise caused by poor ventilation inside the UPS2000-G-6 kVA or UPS2000-G-10 kVA will shorten the service life.
| 5 | Check that the neutral-ground voltage is less than or equal to 5 V AC.
6
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3 |  | 万用表
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.1 |  | Rack-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel |  |  | AB |  | 30min
Installation Procedure
| 1 | Install mounting ears on both sides of the UPS2000-G-6 kVA or UPS2000-G-10 kVA according to instructions. Determine the position for installing the UPS2000-G-6 kVA or UPS2000-G-10 kVA based on its dimensions for rack-mounting.
| 2 | Install adjustable guide rails or floating nuts.
| 3 | Place the UPS on the guide rails. Secure the UPS to the rack using M6x16TM screws through the holes in the mounting brackets.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
2
3
4
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 4 |  |  |  | 4
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-6 kVA or UPS2000-G-10 kVA
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.2/1.4.1 |  | Connecting power cables |  |  | AB |  | 40min
Installation Procedure
| 1 | Open UPS AC input circuit breaker,loosen screws to remove the terminal cover and battery port cover.
| 2 | Connect cables in this sequence: AC output power cables, AC input power cables, and battery cables.
3
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | In a parallel system, connect the loads to AC OUTPUT pL, instead of sL.
| 3 | In a parallel system equipped with no PDU, configure input and output circuit breakers for each UPS before starting the UPSs.
| 4 | Install a DC circuit breaker between the battery string and the UPS battery port.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Battery cables |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.4.2/1.5.1 |  | Connecting communications cables |  |  | AB |  | 20min
Installation Procedure
| 1 | Connect parallel communications cables.
| 2 | (Optional) Connect cables to SNMP card: a. Temperature and humidity monitoring port (TEM_HUM): Connect one end of the cable to the temperature and humidity monitoring port on the Simple Network Management Protocol (SNMP) card and the other end to the ambient temperature and humidity sensor. b. Fast Ethernet (FE) port: Connect one end of the cable to the FE port on the SNMP card and the other end to the Ethernet.
| 3 | (Optional) Connect cables to modbus card: a. Connect the COM_1 port (the COM_2 port is used for cascading) on the Modbus card to the RS485 port on the RS232-RS485 adapter over an RS485 cable. b. Connect the RS232 port on the RS232-RS485 adapter to the RS232 port on the PC over an RS232 cable.
| 4 | (Optional) Connect cables to dry contact card card: Connect one end of the cable to the dry contact card and the other end to the customer equipment.
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
| 2 | In the figure of modbus car, the two UPSs represent two separate single UPS systems.
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.5.2/1.6.1 |  | Connecting the emergency power-off (EPO) switch |  |  | AB |  | 10min
Installation Procedure
| 1 | Connect cables to EPO ports. This procedure is required if the UPS2000-G-6 kVA or UPS2000-G-10 kVA is configured with components that enable the EPO function.
2
3
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.6.2 |  | ower-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel |  |  | AB |  | 30min
Installation Procedure
| 1 | Adjust the control panel and logo directions. Press the grooves on both sides of the front panel, and remove the front panel horizontally with even force. Rotate the control panel 90 degrees anticlockwise. Reinstall the front panel. Rotate the logo on the front panel 90 degrees anticlockwise.
| 2 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically, as shown in the following figure.
| 3 | Install two groups of support bases for each group of devices as follows: Place support bases on the floor, determine the distance (greater than or equal to 280 mm) between the two groups of support bases, place devices on the support bases in sequence, and secure them.
| 4 | After the UPS is tower-mounted, seal the four screw holes on the top with rubber plugs that are delivered with the UPS.
5
6
Key Techniques
| 1 | To ensure that the UPS2000-G-6 kVA or UPS2000-G-10 kVA attaches firmly to the bases, a distance of at least 280 mm is recommended for two neighboring bases. The distance should not exceed the UPS2000-G1-6K or UPS2000-G1-10K depth.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | UPS2000-G-6 kVA or UPS2000-G-10 kVA |  |  | 2 | UPS2000-G-6 kVA or UPS2000-G-10 kVA support bases
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.7 |  | Checking Before Powering On the UPS |  |  | AB |  | 20min
Installation Procedure
| 1 | AC power cable colors comply with local electrical regulations.
| 2 | Cables are securely connected.
| 3 | The battery terminals are connected correctly, and the voltages comply with industry standards.
| 4 | Power cables and signal cables are correctly identified.
| 5 | Cables are neatly routed and securely bound.
| 6 | Devices are installed and cables are routed in ways that facilitate modification, capacity expansion, and maintenance.
| 7 | The UPS is properly grounded.
| 8 | The voltage between the neutral wire and the ground cable is less than 5 V AC.
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.81 |  | 市电启动/参数设置 |  |  | AB |  | 100min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Close the AC input circuit breaker K1.The initialization screen is displayed.Set the language (the preset language is English), system parameters, and battery parameters.Set the single UPS mode (preset) to the parallel mode.
| 3 | Start the UPS in normal mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | The preset password is 000001. The password is used to enter the Settings menu.
| 2 | The default feature code is 999999. The feature code is used to restore the preset password.
| 3 | After you perform "startup operations" on UPS 1 to UPS n one by one, UPS 1 to UPS n are starting. If you do not perform "startup operations" on the other UPSs in 5 minutes, UPS 1 to UPS n enter normal mode, and the other UPSs supply no power.
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-6 kVA devices or UPS2000-G-10 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.2 |  | Starting the UPS in Battery Mode |  |  | AB |  | 100min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Press . The initialization screen is displayed. Set the language (the preset language is English), system parameters, and battery parameters.
| 3 | Perform "startup operations" on the UPS.The UPS enters battery mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | The preset password is 000001. The password is used to enter the Settings menu.
| 2 | The default feature code is 999999. The feature code is used to restore the preset password.
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
面
划线辅助板板
划线辅助板板
Power Cables for the UPS2000-G-6 kVA (Single-Phase Input Single-Phase Output) Equipped with No PDU
Connecting Power Cables to the UPS2000-G-10 kVA (Single-Phase Input Single-Phase Output) Equipped with No PDU
Connecting Power Cables to the UPS2000-G-10 kVA (Three-Phase Input Single-Phase Output) Equipped with No PDU
Connecting Power Cables to the UPS2000-G-10 kVA (Single-Phase Input Single-Phase Output) Equipped with a PDU
Connect parallel communications cables
Connecting Power Cables to the UPS2000-G-6 kVA (Single-Phase Input Single-Phase Output) Equipped with a PDU
Connect cables to SNMP card
Connect cables to modbus card
Connect cables to dry contact card card

## Single UPS 15kVA or 20kVA
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Installation preparations and environment acceptance |  |  | AB |  | 10min
Preparations
| 1 | Install cable trays properly in the equipment room.
| 2 | Check the installation position and direction of the cabinet, make sure it does not interfere with maintenance space of surrounding equipment, and place equipment along the same line to facilitate cabling and maintenance.
| 3 | Install the UPS2000-G-15 kVA or UPS2000-G-20 kVA in environments with proper ventilation and far away from water, heat sources, and flammable or explosive materials. Check that the UPS2000-G-6 kVA or UPS2000-G-10 kVA is free from direct sunlight, dust, volatile gases, corrosive materials, and salty air.
| 4 | Check that the front and rear panels are at least 60 cm away from walls and adjacent equipment. Check that the ventilation holes in the front and rear panels are not blocked. Temperature rise caused by poor ventilation inside the UPS2000-G-15 kVA or UPS2000-G-20 kVA will shorten the service life.
| 5 | Check that the neutral-ground voltage is less than or equal to 5 V AC.
6
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.1 |  | Rack-mounting UPS2000-G-6 kVA devicesor UPS2000-G-10 kVA devices in parallel |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting ears on both sides of the UPS2000-G-6 kVA or UPS2000-G-10 kVA according to instructions. Determine the position for installing the UPS2000-G-6 kVA or UPS2000-G-10 kVA based on its dimensions for rack-mounting.
| 2 | Install adjustable guide rails or floating nuts.
| 3 | Place the UPS on the guide rails. Secure the UPS to the rack using M6x16TM screws through the holes in the mounting brackets.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | When an information and communications technology (ICT) device shares a cabinet with the UPS and is installed above the UPS, the ICT device should not be deeper than 650 mm. Otherwise, keep an appropriate distance between them to facilitate UPS maintenance.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Remove rings, watches, and other metal objects before you move a battery pack.
| 6 | Do not touch uninsulated battery terminals. Otherwise, electric shocks may occur.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 | Flat-head screwdriver (2 mm x 80 mm) |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.2/1.4.1 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Open the circuit breaker of the external battery pack or battery rack (if there is), load circuit breaker, front-end input circuit breaker, and UPS AC input circuit breaker.
| 2 | Loosen screws to remove the terminal covers and battery terminal cover.
| 3 | Connect cables in this sequence: AC output power cables, AC input power cables, and battery cables.
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | In single UPS mode, AC OUTPUT sL connects to primary loads, which require uninterruptible power supply, and pL connects to secondary loads, which require high quality power supply.
| 3 | Install a DC circuit breaker between the battery string and the UPS battery port.
| 4 | In single UPS mode, if power segment is enabled, pL is disconnected and sL continues with power output when an overload occurs
| 5 | Reinstall terminal covers in this sequence: connect the AC INPUT cable and the lower PE cable, install terminal cover 2, connect the AC OUTPUT cable and the upper PE cable, and reinstall terminal cover 1.
| 6 | When you install input and output power cables and battery cables, route the screws through OT terminal holes. Press the cross recessed pan heads of the screws using a torque screwdriver. Align the screws with the screw holes and tighten the screws.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Battery cables |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.4.2/1.5.1 |  | Connecting communications cables |  |  | AB |  | 10min
Installation Procedure
| 1 | (Optional) Connect cables to SNMP card: a. Temperature and humidity monitoring port (TEM_HUM): Connect one end of the cable to the temperature and humidity monitoring port on the Simple Network Management Protocol (SNMP) card and the other end to the ambient temperature and humidity sensor. b. Fast Ethernet (FE) port: Connect one end of the cable to the FE port on the SNMP card and the other end to the Ethernet.
| 2 | (Optional) Connect cables to modbus card: a. Connect the COM_1 port (the COM_2 port is used for cascading) on the Modbus card to the RS485 port on the RS232-RS485 adapter over an RS485 cable. b. Connect the RS232 port on the RS232-RS485 adapter to the RS232 port on the PC over an RS232 cable.
| 3 | (Optional) Connect cables to dry contact card card: Connect one end of the cable to the dry contact card and the other end to the customer equipment.
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
| 2 | In the figure of modbus car, the two UPSs represent two separate single UPS systems.
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.5.2/1.6.1 |  | Connecting the emergency power-off (EPO) switch |  |  | AB |  | 10min
Installation Procedure
| 1 | Connect cables to EPO ports. This procedure is required if the UPS2000-G-6 kVA or UPS2000-G-10 kVA is configured with components that enable the EPO function.
2
3
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.6.2 |  | Tower-mounting a single UPS2000-G-15K or UPS2000-G-20K |  |  | AB |  | 15min
Installation Procedure
| 1 | Adjust the control panel and logo directions. Press the grooves on both sides of the front panel, and remove the front panel horizontally with even force. Rotate the control panel 90 degrees anticlockwise. Reinstall the front panel. Rotate the logo on the front panel 90 degrees anticlockwise.
| 2 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically, as shown in the following figure.
| 3 | Install two groups of support bases for each group of devices as follows: Place support bases on the floor, determine the distance (greater than or equal to 280 mm) between the two groups of support bases, place devices on the support bases in sequence, and secure them.
| 4 | After the UPS is tower-mounted, seal the four screw holes on the top with rubber plugs that are delivered with the UPS.
5
6
Key Techniques
| 1 | To ensure that the UPS2000-G-6 kVA or UPS2000-G-10 kVA attaches firmly to the bases, a distance of at least 280 mm is recommended for two neighboring bases. The distance should not exceed the UPS2000-G1-6K or UPS2000-G1-10K depth.
| 2 | Before operating the control panel, ensure that all power supplies are disconnected.
| 3 | Ground the PE terminal on the rear panel of the UPS.
| 4 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically.
| 5 | When you tower-mount the UPS, place it horizontally during cable connection. Stand it upright after cable installation.
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | UPS2000-G-15 kVA or UPS2000-G-20 kVA |  |  | 2 | UPS2000-G-15 kVA or UPS2000-G-20 kVA support bases
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.7 |  | Checking Before Powering On the UPS |  |  | AB |  | 20min
Installation Procedure
| 1 | AC power cable colors comply with local electrical regulations.
| 2 | Cables are securely connected.
| 3 | The battery terminals are connected correctly, and the voltages comply with industry standards.
| 4 | Power cables and signal cables are correctly identified.
| 5 | Cables are neatly routed and securely bound.
| 6 | Devices are installed and cables are routed in ways that facilitate modification, capacity expansion, and maintenance.
| 7 | The UPS is properly grounded.
| 8 | The voltage between the neutral wire and the ground cable is less than 5 V AC.
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.1 |  | Starting the UPS in Normal Mode |  |  | AB |  | 20min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Close the AC input circuit breaker (K for one mains input,K1and K4 for two mains input) .The initialization screen is displayed.Set the language (the preset language is English), system parameters, and battery parameters.Set the single UPS mode (preset) to the parallel mode.
| 3 | Start the UPS in normal mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | To prevent triggering overload protection, start the loads with higher power and then loads with lower power.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Rack-mounting a single UPS2000-G-15 kVA or UPS2000-G-20 kVA | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.2 |  | Starting the UPS in Battery Mode |  |  | AB |  | 20min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Press .The initialization screen is displayed. Set the language (the preset language is English), system parameters, and battery parameters.
| 3 | Perform "startup operations" on the UPS.The UPS enters battery mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | To prevent triggering overload protection, start the loads with higher power and then loads with lower power.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
B
C
A
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
划线辅助板板
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
第3步
第6步
安装绝缘垫片.
安装螺栓、弹垫、平垫在绝缘垫片上.
安装螺栓、弹垫、平垫在绝缘垫片上.
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and One Mains Inputs)
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and Two Mains Input)
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and One Mains Input)
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and Two Mains Inputs)
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Single-Phase Input Single-Phase Output and One Mains Input)
Connect cables to SNMP card
Connect cables to modbus card
Connect cables to dry contact card card

## 15kVA or 20kVA in parallel
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Installation preparations and environment acceptance |  |  | AB |  | 10min
Preparations
| 1 | Install cable trays properly in the equipment room.
| 2 | Check the installation position and direction of the cabinet, make sure it does not interfere with maintenance space of surrounding equipment, and place equipment along the same line to facilitate cabling and maintenance.
| 3 | Install the UPS2000-G-15 kVA or UPS2000-G-20 kVA in environments with proper ventilation and far away from water, heat sources, and flammable or explosive materials. Check that the UPS2000-G-6 kVA or UPS2000-G-10 kVA is free from direct sunlight, dust, volatile gases, corrosive materials, and salty air.
| 4 | Check that the front and rear panels are at least 60 cm away from walls and adjacent equipment. Check that the ventilation holes in the front and rear panels are not blocked. Temperature rise caused by poor ventilation inside the UPS2000-G-15 kVA or UPS2000-G-20 kVA will shorten the service life.
| 5 | Check that the neutral-ground voltage is less than or equal to 5 V AC.
6
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 | Multimeter |  | 2 |  |  | 3 |  | 万用表
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.1 |  | Rack-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel |  |  | AB |  | 30min
Installation Procedure
| 1 | Install mounting ears on both sides of the UPS2000-G-6 kVA or UPS2000-G-10 kVA according to instructions. Determine the position for installing the UPS2000-G-6 kVA or UPS2000-G-10 kVA based on its dimensions for rack-mounting.
| 2 | Install adjustable guide rails or floating nuts.
| 3 | Place the UPS on the guide rails. Secure the UPS to the rack using M6x16TM screws through the holes in the mounting brackets.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | When an information and communications technology (ICT) device shares a cabinet with the UPS and is installed above the UPS, the ICT device should not be deeper than 650 mm. Otherwise, keep an appropriate distance between them to facilitate UPS maintenance.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Remove rings, watches, and other metal objects before you move a battery pack.
| 6 | Do not touch uninsulated battery terminals. Otherwise, electric shocks may occur.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 3 |  |  |  | 4
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.2/1.4.1 |  | Connecting power cables |  |  | AB |  | 40min
Installation Procedure
| 1 | Open the circuit breaker of the external battery pack or battery rack (if there is), load circuit breaker, front-end input circuit breaker, and UPS AC input circuit breaker.
| 2 | Loosen screws to remove the terminal covers and battery terminal cover.
| 3 | Connect cables in this sequence: AC output power cables, AC input power cables, and battery cables.
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | In a parallel system, connect the loads to AC OUTPUT pL, instead of sL.
| 3 | After cable connection, close the bypass input circuit breaker. Use a multimeter to check whether the voltage between sL terminals on the UPSs is less than 1 V. If the voltage is greater than 1 V, check whether the input phase sequences are the same on each UPS.
| 4 | In a parallel system equipped with no PDU, configure input and output circuit breakers for each UPS before starting the UPSs.
| 5 | Install a DC circuit breaker between the battery string and the UPS battery port.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Battery cables |  |  | 4
| 5 |  |  |  | 6
| 7 |  |  |  | 8
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.4.2/1.5.1 |  | Connecting communications cables |  |  | AB |  | 20min
Installation Procedure
| 1 | Connect parallel communications cables.
| 2 | (Optional) Connect cables to SNMP card: a. Temperature and humidity monitoring port (TEM_HUM): Connect one end of the cable to the temperature and humidity monitoring port on the Simple Network Management Protocol (SNMP) card and the other end to the ambient temperature and humidity sensor. b. Fast Ethernet (FE) port: Connect one end of the cable to the FE port on the SNMP card and the other end to the Ethernet.
| 3 | (Optional) Connect cables to modbus card: a. Connect the COM_1 port (the COM_2 port is used for cascading) on the Modbus card to the RS485 port on the RS232-RS485 adapter over an RS485 cable. b. Connect the RS232 port on the RS232-RS485 adapter to the RS232 port on the PC over an RS232 cable.
| 4 | (Optional) Connect cables to dry contact card card: Connect one end of the cable to the dry contact card and the other end to the customer equipment.
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
| 2 | In the figure of modbus car, the two UPSs represent two separate single UPS systems.
| 3 | Install two parallel cables for a 1+1 parallel system.
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.5.2/1.6.1 |  | Connecting the emergency power-off (EPO) switch |  |  | AB |  | 10min
Connecting the emergency power-off (EPO) switch
| 1 | Connect cables to EPO ports. This procedure is required if the UPS2000-G-6 kVA or UPS2000-G-10 kVA is configured with components that enable the EPO function.
2
3
4
5
6
Key Techniques
| 1 | Connect cables to corresponding ports securely.
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.6.2 |  | Tower-mounting UPS2000-G-15 kVA devicesor UPS2000-G-20 kVA devices in parallel |  |  | AB |  | 30min
Installation Procedure
| 1 | Adjust the control panel and logo directions. Press the grooves on both sides of the front panel, and remove the front panel horizontally with even force. Rotate the control panel 90 degrees anticlockwise. Reinstall the front panel. Rotate the logo on the front panel 90 degrees anticlockwise.
| 2 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically, as shown in the following figure.
| 3 | Install two groups of support bases for each group of devices as follows: Place support bases on the floor, determine the distance (greater than or equal to 280 mm) between the two groups of support bases, place devices on the support bases in sequence, and secure them.
| 4 | After the UPS is tower-mounted, seal the four screw holes on the top with rubber plugs that are delivered with the UPS.
5
6
Key Techniques
| 1 | To ensure that the UPS2000-G-6 kVA or UPS2000-G-10 kVA attaches firmly to the bases, a distance of at least 280 mm is recommended for two neighboring bases. The distance should not exceed the UPS2000-G1-6K or UPS2000-G1-10K depth.
| 2 | Before operating the control panel, ensure that all power supplies are disconnected.
| 3 | Ground the PE terminal on the rear panel of the UPS.
| 4 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically.
| 5 | When you tower-mount the UPS, place it horizontally during cable connection. Stand it upright after cable installation.
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | UPS2000-G-15 kVA or UPS2000-G-20 kVA |  |  | 2 | UPS2000-G-15 kVA or UPS2000-G-20 kVA support bases
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.7 |  | Checking Before Powering On the UPS |  |  | AB |  | 20min
Installation Procedure
| 1 | AC power cable colors comply with local electrical regulations.
| 2 | Cables are securely connected.
| 3 | The battery terminals are connected correctly, and the voltages comply with industry standards.
| 4 | Power cables and signal cables are correctly identified.
| 5 | Cables are neatly routed and securely bound.
| 6 | Devices are installed and cables are routed in ways that facilitate modification, capacity expansion, and maintenance.
| 7 | The UPS is properly grounded.
| 8 | The voltage between the neutral wire and the ground cable is less than 5 V AC.
Key Techniques
1
2
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.81 |  | Starting the UPS in Normal Mode |  |  | AB |  | 100min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Close the AC input circuit breaker (K，K1，K2，Q1，Q2 for one mains input,for two mains input).The initialization screen is displayed.Set the language (the preset language is English), system parameters, and battery parameters.Set the single UPS mode (preset) to the parallel mode.
| 3 | Start the UPS in normal mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | Ensure that the UPSs in the parallel system have the same output voltage.
| 2 | Perform "startup operations" after UPS parallel output (that is, circuit breakers Q2 and Q3 are closed).
| 3 | Before starting the parallel system, do not start loads.
| 4 | To prevent triggering overload protection, start the loads with higher power and then loads with lower power. 备，后开启小功率设备。
| 5 | The preset password is 000001. The password is used to enter the Settings menu.
| 6 | The default feature code is 999999. The feature code is used to restore the preset password.
| 7 | After you perform "startup operations" on UPS 1 to UPS n one by one, UPS 1 to UPS n are starting. If you do not perform "startup operations" on the other UPSs in 5 minutes, UPS 1 to UPS n enter normal mode, and the other UPSs supply no power.
8
9
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing UPS2000-G-15 kVA devices or UPS2000-G-20 kVA devices in parallel | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.8.2 |  | Starting the UPS in Battery Mode |  |  | AB |  | 100min
Installation Procedure
| 1 | Close the external battery circuit breaker (if there is).
| 2 | Press . The initialization screen is displayed. Set the language (the preset language is English), system parameters, and battery parameters.
| 3 | Perform "startup operations" on the UPS.The UPS enters battery mode.
| 4 | When the UPS runs properly, close the UPS AC output circuit breaker Q1, and start the loads.
5
6
Key Techniques
| 1 | The preset password is 000001. The password is used to enter the Settings menu.
| 2 | The default feature code is 999999. The feature code is used to restore the preset password.
3
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
面
划线辅助板板
划线辅助板板
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and Two Mains Inputs) Equipped with a PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and One Mains Input) Equipped with a PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and Two Mains Inputs) Equipped with a PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and One Mains Input) Equipped with a PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Single-Phase Input Single-Phase Output and One Mains Input) Equipped with a PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and Two Mains Inputs) Equipped with No PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Three-Phase Output and One Mains Input) Equipped with No PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and Two Mains Inputs) Equipped with No PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Three-Phase Input Single-Phase Output and One Mains Input) Equipped with No PDU
Connecting Cables to the UPS2000-G-15 kVA/20 kVA (Single-Phase Input Single-Phase Output and One Mains Input) Equipped with No PDU
Connect parallel communications cables
B
C
A
Connect cables to SNMP card
Connect cables to modbus card
Connect cables to dry contact card card

## Installing battery pack
Installing battery pack (ESS-240V12-(9AhBPVBA and 7AhBPVBA)) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing battery pack (ESS-240V12-(9AhBPVBA and 7AhBPVBA)) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2.1 |  | Rack-mounting |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting brackets.
| 2 | Install a cable distribution box.A cable distribution box is an optional component for a battery pack. There is a reserved position for the cable distribution box on the back panel of the battery pack.
| 3 | Install adjustable guide rails and floating nuts.
| 4 | Place the battery pack on the guide rails. Secure the battery pack to the rack using M6x16TM screws through the holes in the mounting bracket.
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | Before you install guide rails, accurately calculate the distance between the upper and lower guide rails.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Do not move the battery pack by holding its mounting brackets, front panel, or terminal cover.
| 6 | Remove rings, watches, and other metal objects before you move a battery pack.
| 7 | Do not touch uninsulated battery terminals. Otherwise, electric shocks may occur.
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 4 |  |  |  | 4
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
Installing battery pack (ESS-240V12-(9AhBPVBA and 7AhBPVBA)) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2.2/1.3.1 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Open the circuit breaker of the external battery pack or battery rack (if there is), load circuit breaker, front-end input circuit breaker, and UPS AC input circuit breaker.
| 2 | (Optional) Remove the cable distribution box cover. This step is performed only for the UPS2000-G-15 kVA and UPS2000-G-20 kVA.
| 3 | Connect cables.
4
5
6
Key Techniques
| 1 | When connecting cables, first connect cables to the cable distribution box and the UPS, and then insert the cables to terminals on the battery cabinet. When removing cables, first disconnect the cables from the battery cabinet, and then cables from the cable distribution box and the UPS.
| 2 | Determine cable colors based on industry standards.
| 3 | One terminal of the cable between the cable distribution box terminal and the UPS BATT.240 V DC terminal is a common OT terminal connecting to the cable distribution box, and the other is the 90° 16 mm² M6 OT terminal connecting to the UPS. (See battery cable 03 mentioned in the following table.)
| 4 | . The screw specifications for the cable distribution box terminal are M6x14. The required torque for tightening power cables is 5 N·m, and a torque screwdriver is recommended.
5
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | Battery cable |  |  | 2
| 3 |  |  |  | 4
| 5 |  |  |  | 6
Installing battery pack (ESS-240V12-(9AhBPVBA and 7AhBPVBA)) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3.2 |  | Tower-mounting |  |  | AB |  | 15min
Installation Procedure
| 1 | Assemble support bases. When you assemble two support bases, align connecting buckles with holes and insert the buckles vertically, as shown in the following figure.
| 2 | Install two groups of support bases for each group of battery packs as follows: Place support bases on the floor, determine the distance (greater than or equal to 280 mm) between the two groups of support bases, place battery packs on the support bases in sequence, and secure them.
| 3 | After the battery packs are tower-mounted, seal the four screw holes on the top with rubber plugs that are delivered with the battery packs.
4
5
6
Key Techniques
| 1 | To ensure that the battery pack attaches firmly to the bases, a distance of at least 280 mm is recommended for two neighboring bases. The distance should not exceed the UPS2000-G1-6K or UPS2000-G1-10K depth.
| 2 | The support base length is adjustable. You can add components to increase the length.
| 3 | Exert force to disassemble components in the reverse directions of assembling.
4
Installation Tools/Tooling
| 1 |  |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | Battery pack |  |  | 2 | Support bases
| 3 |  |  |  | 4
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
面
划线辅助板板
划线辅助板板
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步

## Installing PDU(PDC-0091V2ACIOA)
Installing PDU (PDC-0091V2ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing PDU (PDC-0091V2ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Rack-mounting |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting brackets.
| 2 | Install adjustable guide rails and floating nuts.
| 3 | Place the battery pack on the guide rails. Secure the battery pack to the rack using M6x16TM screws through the holes in the mounting bracket.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | Before you install guide rails, accurately calculate the distance between the upper and lower guide rails.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Do not move the battery pack by holding its mounting brackets, front panel, or terminal cover.
6
7
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 4 |  |  |  | 4
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
| 3 | Rack |  |  | 4 | PDU
Installing PDU (PDC-0091V2ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Remove the front panel from the PDU and open the circuit breakers.
| 2 | Loosen screws to remove the busbar cover.
| 3 | Connect cables.
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | In a parallel system, connect the loads to AC OUTPUT pL, instead of sL.
3
4
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Cables between PDU and UPS |  |  | 4 | Maintenance bypass port cable
| 5 | CAN communications port cable |  |  | 6
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
划线辅助板板
划线辅助板板
Connecting cables to the PDU for a 1+1 or 2+0 UPS2000-G-6 kVA/10 kVA parallel system (single-phase input single-phase output)
Connecting cables to the PDU for a 1+1 UPS2000-G-15 kVA/20 kVA parallel system (Three-phase input single-phase output and Two Mains Input)
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
Connecting cables to the PDU for a 1+1 UPS2000-G-15 kVA/20 kVA parallel system (single-phase input single-phase output)
Connecting cables to the PDU for a 1+1 UPS2000-G-15 kVA/20 kVA parallel system (Three-phase input single-phase output and One Mains Input)

## Installing PDU(PDC-0038V4ACIOA)
Installing PDU (PDC-0038V4ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing PDU (PDC-0038V4ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Rack-mounting |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting brackets.
| 2 | Install adjustable guide rails and floating nuts.
| 3 | Place the battery pack on the guide rails. Secure the battery pack to the rack using M6x16TM screws through the holes in the mounting bracket.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | Before you install guide rails, accurately calculate the distance between the upper and lower guide rails.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Do not move the battery pack by holding its mounting brackets, front panel, or terminal cover.
6
7
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 4 |  |  |  | 4
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
| 3 | Rack |  |  | 4 | PDU
Installing PDU (PDC-0038V4ACIOA) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Remove the front panel from the PDU and open the circuit breakers.
| 2 | Loosen screws to remove the busbar cover.
| 3 | Connect cables.
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | In a parallel system, connect the loads to AC OUTPUT pL, instead of sL.
3
4
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 | Cables between PDU and UPS |  |  | 4 | Maintenance bypass port cable
| 5 | CAN communications port cable |  |  | 6
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
划线辅助板板
划线辅助板板
Connecting Cables to the PDU for a 1+1 UPS2000-G-15 kVA/20 kVA Parallel System (Three-Phase Input Three-Phase Output)
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步

## Installing Transformer
Installing Industrial-Frequency Transformer(DGL-6 & DGL-10) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.1 |  | Unpacking and checking |  |  | AB |  | 10min
Preparations
| 1 | Unpack equipment onsite.
| 2 | Check the total number and packing of devices based on the packing list after auxiliary materials such as storage batteries, are delivered to the installation site.
| 3 | Verify that the components in the packing boxes consist with the packing list and then sign on the packing list with the customer.
| 4 | Check whether the devices are damaged. If any damages are found, notify the carrier immediately.
5
6
Key Techniques
| 1 | Move the unpacked devices indoors for proper storage.
| 2 | Verify the number of materials and then sign with the customer on the packing list.
3
4
Installation Tools/Tooling
| 1 | Flat-head screwdriver (2 mm x 80 mm) |  | 2 | Claw hammer |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 |  |  |  | 2
| 3 |  |  |  | 4
Installing Industrial-Frequency Transformer(DGL-6 & DGL-10) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.2 |  | Rack-mounting |  |  | AB |  | 15min
Installation Procedure
| 1 | Install mounting brackets.
| 2 | Install adjustable guide rails and floating nuts.
| 3 | Place the battery pack on the guide rails. Secure the battery pack to the rack using M6x16TM screws through the holes in the mounting bracket.
4
5
6
Key Techniques
| 1 | Four M6x16 screws and M6 floating nuts are required.
| 2 | Install adjustable guide rails when you rack-mount a device. For a 2 U device, install only adjustable guide rails and secure it with screws. For a 3 U device, install adjustable guide rails and two floating nuts and secure them with screws. The floating nuts are delivered with the rack.
| 3 | Before you install guide rails, accurately calculate the distance between the upper and lower guide rails.
| 4 | Ensure that the rack is properly grounded before the operation.
| 5 | Do not move the battery pack by holding its mounting brackets, front panel, or terminal cover.
6
7
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  |  | 2 | Flat-head screwdriver (2 mm x 80 mm)
| 3 |  |  |  | 4
Installation Materials
Installation Materials
| 1 | M6x16 screws |  |  | 2 | M6 floating nut
| 3 | Rack |  |  | 4 | UPS2000-G-15 kVA or UPS2000-G-20 kVA
| 3 | Rack |  |  | 4 | Industrial-Frequency Transformer(DGL-6 & DGL-10)
Installing Industrial-Frequency Transformer(DGL-6 & DGL-10) | No. |  | Operation |  |  | Operator |  | Operation Time
| 1.3 |  | Connecting power cables |  |  | AB |  | 25min
Installation Procedure
| 1 | Loosen screws to remove the input and output terminal protective covers.
| 2 | Connect cables.
3
4
5
6
Key Techniques
| 1 | Connect input power cables to input terminals and output power cables to output terminals correctly and securely.
| 2 | When you connect a transformer on the system output side, connect the load to the pL terminal and disable hierarchical disconnection. Set parameters on the LCD as follows: 1. Choose Main Menu > Settings > System Parameters > Others. Set Output transformer to Enabled. 2. Choose Main Menu > Settings > System Parameters > Power Segment. Set Power segment to Disabled
| 3 | Prepare the input and output power cables onsite. The recommended cross-sectional area is 6 mm². The temperature switch is delivered with the transformer.
| 4 | In the case of 110 V parallel output, short-circuit L1 and L2 and short-circuit N1 and N2. Ensure that the L1 and L2 cables are of an equal length, and N1 and N2 cables are of an equal length.
| 5 | For 220 V output, use a short-circuit busbar to short-circuit N1 and L2.
| 6 | The cable colors must comply with the local industry standards.. If the customer purchases input and output power cables from other manufacturers, use the cables that comply with the standards such as Underwriter Laboratory (UL) or International Electrotechnical Commission (IEC).
Installation Tools/Tooling
| 1 | Phillips screwdriver (2 mm x 150 mm or PH 3 mm x 250 mm) |  | 2 |  |  | 3
| 4 |  |  | 5 |  |  | 6
Installation Materials
| 1 | AC input power cables |  |  | 2 | AC output power cables
| 3 |  |  |  | 4
第3步
第6步
划线辅助板板
第3步
第6步
第3步
第6步
第3步
第6步
面
划线辅助板板
划线辅助板板
划线辅助板板
划线辅助板板